## Govindpuram
GHAZIABAD DOVELOPMENT AUTHORITY
NAME OF SITE :- 56MLD SEWAGE TREATMENT PLANT
LOCATION :- GOVINDPURAM GHAZIABAD
AGENCY :- M/S VIBHOR VAIBHAV INFRA (P)LTD
OPERATION & MAINTENANCE :-1JULY-2021 TO 31-OCTOBER-2021
MONTH AND YEAR:- NOVEMBER 2021
DATE | INLET | OUTLET |  | INLET PARAMETERS |  |  |  | MLSS | MLVSS | OUTLET PARAMETERS |  |  |  |  | Sludge Generation/Day
| MLD | MLD | PH | TSS | COD | BOD | DO | Mg/l | Mg/l | PH | TSS | COD | BOD | DO
2021-01-11 | 25.35 | 24.52 | 7.43 | 85 | 285 | 92.8 | 1.04 | 4229 | 2650 | 7.32 | 12 | 56 | 8.7 | 3.71 | 1.027
2021-02-11 | 25.5 | 24.48 | 7.72 | 110 | 305 | 107.2 | 1.09 | 4294 | 2750 | 7.51 | 10 | 40 | 9.1 | 4.2 | 1.026
2021-03-11 | 25.35 | 24.21 | 7.62 | 105 | 300 | 101.4 | 0.96 | 4155 | 2593 | 7.44 | 10 | 56 | 8.9 | 4.36 | 1.063
2021-04-11 | 25.22 | 24.11 | 7.69 | 93 | 326 | 115.9 | 1.03 | 4408 | 2815 | 7.26 | 9 | 48 | 8.6 | 4.11 | 1.025
2021-05-11 | 25.37 | 24.27 | 7.7 | 126 | 296 | 110.3 | 0.9 | 4284 | 2679 | 7.56 | 11 | 42 | 8.2 | 3.94 | 1.018
2021-06-11 | 25.58 | 24.43 | 7.56 | 108 | 344 | 86.5 | 0.79 | 4356 | 2783 | 7.41 | 10 | 64 | 8.6 | 4.16 | 1.021
2021-07-11 | 25.34 | 24.21 | 7.74 | 117 | 272 | 108.6 | 1.09 | 4470 | 2854 | 7.43 | 13 | 40 | 9.1 | 4.36 | 1.025
2021-08-11 | 25.45 | 24.28 | 7.58 | 104 | 328 | 115.4 | 1.03 | 4249 | 2670 | 7.58 | 9 | 36 | 8.7 | 4.08 | 1.029
2021-09-11 | 25.63 | 24.23 | 7.69 | 88 | 306 | 104.2 | 1.07 | 4095 | 2583 | 7.45 | 14 | 52 | 8.4 | 4.21 | 1.026
2021-10-12 | 25.38 | 24.37 | 7.66 | 126 | 292 | 96.9 | 0.95 | 4352 | 2772 | 7.39 | 11 | 48 | 9.2 | 4.16 | 1.062
2021-11-13 | 25.59 | 24.32 | 7.49 | 105 | 344 | 90.5 | 1.05 | 4193 | 2634 | 7.23 | 10 | 58 | 8.8 | 4.38 | 1.059
2021-12-14 | 25.32 | 24.49 | 7.72 | 93 | 320 | 114.2 | 1.1 | 4258 | 2746 | 7.41 | 9 | 45 | 8.5 | 4.15 | 1.025
13/11/2021 | 25.91 | 24.87 | 7.68 | 110 | 288 | 105.3 | 1.03 | 4207 | 2629 | 7.5 | 12 | 64 | 8.4 | 3.96 | 1.018
14/11/2021 | 25.46 | 24.49 | 7.55 | 102 | 305 | 117.6 | 0.85 | 4283 | 2736 | 7.44 | 13 | 40 | 8.7 | 4.36 | 1.006
15/11/2021 | 25.47 | 24.53 | 7.63 | 115 | 348 | 102.8 | 1.04 | 3987 | 2472 | 7.59 | 11 | 46 | 8.1 | 4.25 | 1.062
16/11/2021 | 25.48 | 24.58 | 7.49 | 83 | 300 | 126.4 | 1.07 | 4208 | 2693 | 7.52 | 10 | 36 | 9.1 | 4.19 | 1.017
17/11/2021 | 25.46 | 24.49 | 7.66 | 122 | 326 | 105.3 | 0.85 | 4305 | 2715 | 7.28 | 12 | 56 | 8.5 | 4.2 | 1.001
18/11/2021 | 25.3 | 24.11 | 7.59 | 75 | 295 | 110.4 | 0.94 | 4219 | 2625 | 7.44 | 9 | 52 | 8.8 | 4.26 | 0.953
19/11/2021 | 25.41 | 24.39 | 7.71 | 95 | 264 | 98.6 | 1.06 | 4163 | 2493 | 7.36 | 10 | 48 | 8.2 | 4.19 | 0.952
20/11/2021 | 25.9 | 24.83 | 7.53 | 87 | 315 | 108.2 | 1.01 | 4136 | 2615 | 7.48 | 12 | 64 | 8.5 | 3.99 | 0.895
21/11/2021 | 25.64 | 24.59 | 7.7 | 72 | 326 | 97.5 | 1.09 | 4272 | 2743 | 7.41 | 13 | 36 | 8.9 | 4.2 | 0.964
22/11/2021 | 25.42 | 24.38 | 7.61 | 105 | 284 | 104.3 | 1.04 | 4053 | 2561 | 7.55 | 10 | 56 | 8.7 | 4.16 | 1.019
23/11/2021 | 25.53 | 24.35 | 7.49 | 126 | 310 | 89.8 | 0.9 | 4195 | 2683 | 7.28 | 11 | 40 | 9.1 | 4.35 | 1.026
24/11/2021 | 25.34 | 24.16 | 7.68 | 110 | 272 | 105.3 | 1.06 | 4017 | 2605 | 7.52 | 10 | 64 | 8.8 | 4.2 | 1.034
25/11/2021 | 25.73 | 24.64 | 7.45 | 91 | 300 | 109.4 | 1.13 | 4137 | 2675 | 7.39 | 12 | 40 | 8.4 | 3.99 | 1.025
26/11/2021 | 25.76 | 24.53 | 7.57 | 102 | 326 | 101.9 | 1.02 | 4208 | 2730 | 7.44 | 9 | 48 | 8.7 | 4.11 | 1.024
27/11/2021 | 25.95 | 24.87 | 7.73 | 112 | 294 | 120.8 | 0.93 | 4096 | 2585 | 7.57 | 10 | 52 | 9 | 4.36 | 1.025
28/11/2021 | 25.56 | 24.35 | 7.62 | 117 | 319 | 112.4 | 1.06 | 4153 | 2644 | 7.31 | 12 | 40 | 8.2 | 3.83 | 1.062
29/11/2021 | 25.83 | 24.75 | 7.59 | 84 | 272 | 96.8 | 0.85 | 4277 | 2731 | 7.46 | 11 | 36 | 8.8 | 4.09 | 1.018
30/11/2021 | 25.39 | 24.21 | 7.8 | 103 | 344 | 105.3 | 1.05 | 4270 | 2656 | 7.43 | 11 | 48 | 8.7 | 3.92 | 1.025
Total | 765.62 | [13 empty] | 30.532
GHAZIABAD DOVELOPMENT AUTHORITY
NAME OF SITE :- 56MLD SEWAGE TREATMENT PLANT
LOCATION :- GOVINDPURAM GHAZIABAD
AGENCY :- M/S VIBHOR VAIBHAV INFRA (P)LTD
OPERATION & MAINTENANCE :-1JULY-2021 TO 31-OCTOBER-2021
MONTH AND YEAR:- DECEMBER 2021
DATE | INLET | OUTLET |  | INLET PARAMETERS |  |  |  | MLSS | MLVSS | OUTLET PARAMETERS |  |  |  |  | Desludging /Day
| MLD | MLD | PH | TSS | COD | BOD | DO | Mg/l | Mg/l | PH | TSS | COD | BOD | DO
2021-01-12 | 28.36 | 27.24 | 7.75 | 85 | 284 | 107.3 | 1.02 | 4198 | 2673 | 7.39 | 9 | 56 | 8.2 | 3.91 | 0.852
2021-02-12 | 28.52 | 27.48 | 7.56 | 110 | 326 | 102.5 | 1.06 | 4305 | 2789 | 7.45 | 11 | 48 | 8.9 | 4.21 | 0.858
2021-03-12 | 28.72 | 27.84 | 7.68 | 89 | 305 | 114.2 | 0.95 | 4156 | 2629 | 7.21 | 12 | 36 | 8.4 | 4.36 | 0.859
2021-04-12 | 28.64 | 27.55 | 7.63 | 105 | 292 | 105.6 | 1.04 | 4208 | 2702 | 7.4 | 10 | 40 | 8.1 | 4.19 | 0.841
2021-05-12 | 28.87 | 27.86 | 7.41 | 117 | 300 | 110.3 | 0.95 | 4235 | 2744 | 7.29 | 11 | 52 | 8.6 | 4.2 | 0.838
2021-06-12 | 28.34 | 27.26 | 7.59 | 96 | 272 | 96.4 | 0.83 | 4184 | 2657 | 7.15 | 10 | 48 | 9.2 | 3.95 | 0.852
2021-07-12 | 28.76 | 27.72 | 7.64 | 121 | 346 | 114.6 | 1.05 | 4340 | 2810 | 7.32 | 10 | 40 | 8.5 | 4.16 | 0.837
2021-08-12 | 28.85 | 27.61 | 7.51 | 117 | 292 | 109.2 | 1.09 | 4177 | 2587 | 7.26 | 13 | 56 | 8.7 | 4.49 | 0.845
2021-09-12 | 28.22 | 27.39 | 7.73 | 108 | 302 | 115.8 | 1.14 | 4226 | 2709 | 7.41 | 10 | 40 | 8.2 | 4.31 | 0.874
2021-10-12 | 27.98 | 26.74 | 7.54 | 72 | 325 | 127.4 | 1.03 | 4194 | 2672 | 7.32 | 9 | 64 | 9 | 4.26 | 0.896
2021-11-12 | 28.36 | 27.23 | 7.67 | 103 | 298 | 117.8 | 0.95 | 4255 | 2650 | 7.41 | 10 | 48 | 8.5 | 4.15 | 0.872
2021-12-12 | 28.34 | 27.42 | 7.59 | 127 | 356 | 101.9 | 1.09 | 4288 | 2794 | 7.19 | 12 | 52 | 8.9 | 4.19 | 0.895
13/12/2021 | 28.91 | 27.31 | 7.81 | 89 | 300 | 108.2 | 1.18 | 4256 | 2761 | 7.31 | 11 | 48 | 8.6 | 3.92 | 0.838
14/12/2021 | 28.23 | 26.21 | 7.66 | 115 | 315 | 98.5 | 1.04 | 4309 | 2803 | 7.44 | 9 | 64 | 8.7 | 4.35 | 0.862
15/12/2021 | 28.76 | 26.64 | 7.45 | 102 | 279 | 102.9 | 0.93 | 4217 | 2740 | 7.61 | 10 | 40 | 9 | 4.21 | 0.862
16/12/2021 | 28.7 | 27.68 | 7.72 | 105 | 292 | 116.4 | 0.75 | 4338 | 2819 | 7.26 | 10 | 56 | 8.8 | 4.18 | 0.831
17/12/2021 | 28.75 | 26.34 | 7.6 | 85 | 344 | 102.4 | 1.06 | 4397 | 2876 | 7.46 | 13 | 48 | 9.2 | 3.97 | 0.831
18/12/2021 | 28.84 | 27.62 | 7.49 | 104 | 298 | 107.5 | 1.02 | 4215 | 2740 | 7.39 | 11 | 52 | 8.4 | 4.2 | 0.814
19/12/2021 | 28.75 | 27.83 | 7.58 | 120 | 326 | 94.8 | 0.91 | 4272 | 2770 | 7.55 | 12 | 50 | 8.9 | 4.33 | 0.873
20/12/2021 | 28.98 | 27.72 | 7.49 | 107 | 300 | 112.6 | 0.83 | 4295 | 2761 | 7.36 | 10 | 64 | 8.3 | 4.18 | 0.89
21/12/2021 | 28.84 | 27.68 | 7.71 | 80 | 322 | 105.9 | 1.09 | 4355 | 2885 | 7.21 | 11 | 40 | 8 | 3.91 | 0.893
22/12/2021 | 28.64 | 27.64 | 7.66 | 96 | 286 | 98.3 | 1.04 | 4309 | 2794 | 7.42 | 12 | 48 | 9.1 | 4.31 | 0.89
23/12/2021 | 28.95 | 27.84 | 7.63 | 112 | 305 | 109.8 | 0.95 | 4291 | 2752 | 7.51 | 10 | 39 | 8.4 | 3.82 | 0.893
24/12/2021 | 28.89 | 27.82 | 7.72 | 116 | 272 | 104.3 | 1.05 | 4356 | 2843 | 7.39 | 13 | 48 | 8.6 | 4.16 | 0.831
25/12/2021 | 28.93 | 27.69 | 7.56 | 102 | 325 | 110.4 | 0.91 | 4247 | 2794 | 7.36 | 9 | 56 | 8.9 | 3.75 | 0.814
26/12/2021 | 28.74 | 27.52 | 7.49 | 125 | 345 | 123.5 | 0.82 | 4384 | 2850 | 7.4 | 11 | 40 | 8.2 | 4.15 | 0.748
27/12/2021 | 28.26 | 27.38 | 7.54 | 70 | 284 | 95.8 | 1.04 | 4196 | 2580 | 7.53 | 10 | 48 | 9.1 | 3.95 | 0.873
28/12/2021 | 28.67 | 27.42 | 7.75 | 95 | 292 | 86.9 | 0.9 | 4309 | 2710 | 7.28 | 12 | 36 | 8.7 | 4.2 | 0.893
29/12/2021 | 28.87 | 27.94 | 7.69 | 108 | 326 | 103.2 | 1.09 | 4257 | 2644 | 7.4 | 10 | 54 | 8.9 | 4.08 | 0.815
30/12/2021 | 28.88 | 27.64 | 7.81 | 136 | 344 | 115.2 | 0.93 | 4308 | 2815 | 7.41 | 13 | 56 | 8.4 | 3.91 | 0.805
31/12/2021 | 28.91 | 27.83 | 7.52 | 105 | 319 | 126.5 | 1.12 | 4279 | 2783 | 7.36 | 10 | 48 | 9.1 | 4.23 | 0.853
Total sludge generation | 888.46 | [13 empty] | 26.428
GHAZIABAD DOVELOPMENT AUTHORITY
NAME OF SITE :- 56MLD SEWAGE TREATMENT PLANT
LOCATION :- GOVINDPURAM GHAZIABAD
AGENCY :- M/S VIBHOR VAIBHAV INFRA (P)LTD
OPERATION & MAINTENANCE :-1JULY-2021 TO 31-OCTOBER-2021
MONTH AND YEAR:- JANUARY 2022
DATE | INLET | OUTLET |  | INLET PARAMETERS |  |  |  | MLSS | MLVSS | OUTLET PARAMETERS | [5 empty] | Total Sludge Generation / Day
| MLD | MLD | PH | TSS | COD | BOD | DO | Mg/l | Mg/l | PH | TSS | COD | BOD | DO
2022-01-01 | 28.45 | 27.35 | 7.62 | 118 | 328 | 120.1 | 1.09 | 4196 | 2672 | 7.38 | 14 | 64 | 9.1 | 4.36 | 0.88195 | 0.883
2022-01-02 | 28.21 | 27.14 | 7.49 | 126 | 284 | 118.3 | 1.15 | 4310 | 2685 | 7.45 | 11 | 56 | 8.4 | 4.21 | 0.87451 | 0.882
2022-01-03 | 28.93 | 27.46 | 7.75 | 105 | 340 | 136.4 | 0.95 | 4515 | 2940 | 7.4 | 12 | 36 | 9 | 4.19 | 0.89683 | 0.848
2022-01-04 | 28.83 | 27.74 | 7.6 | 116 | 321 | 105.8 | 1.02 | 4349 | 2792 | 7.55 | 14 | 40 | 8.6 | 4.32 | 0.89373 | 0.887
2022-01-05 | 28.73 | 27.64 | 7.69 | 125 | 300 | 123.5 | 1.06 | 4410 | 2839 | 7.29 | 11 | 45 | 8.8 | 4.4 | 0.89063 | 0.897
2022-01-06 | 28.21 | 27.31 | 7.72 | 136 | 344 | 108.2 | 0.83 | 4088 | 2563 | 7.31 | 12 | 48 | 8.3 | 4.58 | 0.87451 | 0.86
2022-01-07 | 28.37 | 27.32 | 7.48 | 102 | 322 | 132.4 | 1.09 | 4250 | 2672 | 7.6 | 10 | 62 | 8.9 | 4.39 | 0.87947 | 0.898
2022-01-08 | 28.36 | 27.49 | 7.59 | 109 | 298 | 106.5 | 0.98 | 4223 | 2640 | 7.53 | 12 | 50 | 8.2 | 4.2 | 0.87916 | 0.8945
2022-01-09 | 28.67 | 27.59 | 7.78 | 121 | 319 | 117.9 | 1.12 | 4309 | 2681 | 7.34 | 11 | 42 | 8.5 | 3.81 | 0.88877 | 0.863
2022-01-10 | 28.76 | 27.64 | 7.66 | 83 | 305 | 122.1 | 1.08 | 4196 | 2570 | 7.49 | 13 | 40 | 8.9 | 4.18 | 0.89156 | 0.876
2022-01-11 | 28.68 | 27.4 | 7.43 | 102 | 318 | 115.6 | 1.05 | 4208 | 2631 | 7.52 | 10 | 36 | 8.7 | 4.2 | 0.88908 | 0.835
2022-01-12 | 28.62 | 27.53 | 7.54 | 95 | 326 | 126.3 | 1.03 | 4288 | 2708 | 7.35 | 11 | 48 | 8.4 | 4.35 | 0.88722 | 0.881
2022-01-13 | 28.56 | 27.48 | 7.75 | 109 | 358 | 110.5 | 1.14 | 4096 | 2510 | 7.31 | 15 | 64 | 9.1 | 3.97 | 0.88536 | 0.893
2022-01-14 | 28.96 | 27.85 | 7.62 | 126 | 294 | 107.4 | 1.06 | 4108 | 2553 | 7.29 | 10 | 40 | 9.3 | 3.95 | 0.89776 | 0.872
2022-01-15 | 28.75 | 27.48 | 7.81 | 105 | 300 | 121.5 | 1.1 | 4059 | 2483 | 7.45 | 14 | 55 | 8.6 | 4.17 | 0.89125 | 0.862
2022-01-16 | 28.52 | 27.39 | 7.7 | 118 | 272 | 108.5 | 0.95 | 4217 | 2635 | 7.55 | 15 | 40 | 8.4 | 4.09 | 0.88412 | 0.892
2022-01-17 | 28.18 | 27.29 | 7.73 | 103 | 346 | 98.6 | 1.13 | 4155 | 2579 | 7.26 | 12 | 60 | 8.9 | 4.33 | 0.87358 | 0.795
2022-01-18 | 28.48 | 27.63 | 7.59 | 110 | 322 | 117.4 | 1.21 | 4310 | 2609 | 7.48 | 13 | 56 | 9.2 | 4.25 | 0.88288 | 0.897
2022-01-19 | 28.72 | 27.69 | 7.68 | 122 | 296 | 110.8 | 0.86 | 4219 | 2544 | 7.32 | 10 | 42 | 8.2 | 4.3 | 0.89032 | 0.851
2022-01-20 | 28.38 | 27.49 | 7.61 | 135 | 309 | 102.6 | 1.09 | 4136 | 2507 | 7.4 | 14 | 48 | 9 | 4.21 | 0.87978 | 0.891
2022-01-21 | 28.47 | 27.39 | 7.74 | 108 | 340 | 114.9 | 1.06 | 4254 | 2503 | 7.38 | 15 | 52 | 8.6 | 3.96 | 0.88257 | 0.875
2022-01-22 | 28.93 | 27.48 | 7.63 | 95 | 272 | 108.2 | 1.09 | 4308 | 2529 | 7.48 | 13 | 45 | 9.1 | 4.25 | 0.89683 | 0.892
2022-01-23 | 28.97 | 27.83 | 7.6 | 126 | 305 | 122.4 | 1.04 | 4219 | 2546 | 7.41 | 10 | 56 | 8.4 | 4.2 | 0.89807 | 0.899
2022-01-24 | 28.27 | 27.17 | 7.79 | 125 | 296 | 128.3 | 0.93 | 4315 | 2674 | 7.35 | 12 | 40 | 8.7 | 4.18 | 0.87637 | 0.896
2022-01-25 | 28.03 | 26.75 | 7.56 | 117 | 335 | 105.2 | 1.02 | 4267 | 2647 | 7.19 | 16 | 64 | 9.3 | 4.36 | 0.86893 | 0.891
2022-01-26 | 28.62 | 27.35 | 7.58 | 107 | 344 | 107.5 | 0.94 | 4235 | 2586 | 7.54 | 11 | 44 | 8.5 | 3.97 | 0.88722 | 0.837
2022-01-27 | 28.32 | 27.21 | 7.62 | 110 | 300 | 122.8 | 0.86 | 4309 | 2547 | 7.23 | 14 | 38 | 8.9 | 4.4 | 0.87792 | 0.897
2022-01-28 | 28.46 | 27.38 | 7.59 | 105 | 320 | 104.2 | 1.03 | 4155 | 2634 | 7.39 | 12 | 44 | 8.6 | 4.16 | 0.88226 | 0.853
2022-01-29 | 28.48 | 27.35 | 7.71 | 97 | 356 | 116.5 | 1.07 | 4196 | 2578 | 7.44 | 11 | 52 | 8.4 | 4.21 | 0.88288 | 0.891
2022-01-30 | 28.43 | 27.21 | 7.66 | 127 | 327 | 126.3 | 1.06 | 4139 | 2619 | 7.31 | 14 | 52 | 8.9 | 3.99 | 0.88133 | 0.896
2022-01-31 | 28.43 | 24.4 | 7.79 | 109 | 344 | 109.8 | 1.12 | 4256 | 2744 | 7.45 | 11 | 45 | 8.5 | 4.21 | 0.88133 | 0.896
| 884.78 | [13 empty] | 26.5468 | 26.2845